## Help
The following instructions are to assist you in choosing the correct Manual S Form for your design conditions and manufacturer's data.
Form Selection Guide
The Manual S Speedsheet is made up of four individual forms (S-1a through S-1d).
One form must be selected and filled out complete for compliance with Manual S.
Because design conditions and manufacturer's cooling and heating data sets vary, choose the form that best matches your criteria.
All four of the individual Manual S forms have yellow colored cells to input your information, Manual J data and manufacturer's data.
All applicable yellow cells must be filled out for full Manual S compliance.
All applicable dropdown selection cells are colored gray with bold font and must be selected for full Manual S compliance.
Use Form S-1a for two-way interpolation of manufacturer's cooling capacities at outdoor and indoor design conditions.
Exampe: My summer outdoor design is 92 degrees db and my indoor design is 63 degrees wb
The manufacturer's published outdoor data is 85 and 95 degrees db so interpolation is needed to calculate the capacity at 92 degrees db
The manufacturer's published indoor data is 67 and 62 degrees wb so interpolation is needed to calculate the capacity at 63 degrees wb
Use Form S-1b for one-way interpolation of manufacturer's cooling capacities at indoor design conditions.
Exampe: My summer outdoor design is 95 degrees db and my indoor design is 63 degrees wb
The manufacturer's published outdoor data is equal to the design conditions.
The manufacturer's published indoor data is 67 and 62 degrees wb so interpolation is needed to calculate the capacity at 63 degrees wb
Use Form S-1c for one-way interpolation of manufacturer's cooling capacities at outdoor design conditions.
Exampe: My summer outdoor design is 92 degrees db and my indoor design is 63 degrees wb
The manufacturer's published outdoor data is 85 and 95 degrees db so interpolation is needed to calculate the capacity at 92 degrees db
The manufacturer's published indoor data is equal to the design conditions.
Use Form S-1d for no interpolation of manufacturer's cooling capacities at outdoor design conditions.
Exampe: My summer outdoor design is 95 degrees db and my indoor design is 63 degrees wb
The manufacturer's published outdoor data is equal to the design conditions.
The manufacturer's published indoor data is equal to the design conditions.

## Form S-1a
Air Conditioning Contractors of America • Manual S 2nd Edition (2014) Residential Equipment Selection
Project Information |  |  |  |  | Design Information
Name |  |  |  |  | Outdoor Design Temperature - Summer
Address |  |  |  |  | Indoor Design Temperature - Summer
City |  |  |  |  | Indoor Design %RH - Summer
State |  | Zip Code |  |  | Outdoor Design Temperature - Winter
System ID |  |  |  |  | Project Location Elevation |  |  | 0
Proposed Equipment | System Type | Air-Air, Cooling Only, Single-Speed Compressor, Mild Winter or Latent Load
| Manufacturer |  | Furnace # |  |  |  | AFUE
| Manufacturer |  | AHU/Coil # |  |  |  | SEER
| Manufacturer |  | Condenser # |  |  |  | HSPF
| Manufacturer |  | Package # |  |  |  | Fan Speed | Med
Manual J Load Calculations |  |  |  | Heat | Total | Sensible | Latent | SHR
|  |  |  | Loss | BTUH | BTUH | BTUH
[7 empty] | 0 | #DIV/0!
To interpolate capacities, enter the listed capacities from the manufacturers cooling performance charts that are less than the design temperatures here
Out DB per OEM Chart | #N/A |  | Design CFM | Return Air | Total | Sensible | Latent | SHR
In DB per OEM Chart | 0 |  |  | (F wb) | BTUH | BTUH | BTUH
Capacity from MFG table |  |  |  | 68 |  |  | 0 | #DIV/0!
Interpolated Capacity |  |  |  | 63 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
Capacity from MFG table |  |  |  | 62 |  |  | 0 | #DIV/0!
Output from this chart |  |  | 0 | 63 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
To interpolate capacities, enter the listed capacities from the manufacturers cooling performance charts that are greater than the design temperatures here
Out DB per OEM Chart | #N/A |  | Design CFM | Return Air | Total | Sensible | Latent | SHR
In DB per OEM Chart | 0 |  |  | (F wb) | BTUH | BTUH | BTUH
Capacity from MFG table |  |  | 0 | 68 |  |  | 0 | #DIV/0!
Interpolated Capacity |  |  |  | 63 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
Capacity from MFG table |  |  |  | 62 |  |  | 0 | #DIV/0!
Output from this chart |  |  | 0 | 63 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
Out DB per OEM Chart | 0 |  | Design CFM | Return Air | Total | Sensible | Latent | SHR
In DB per OEM Chart | 0 |  |  | (F wb) | BTUH | BTUH | BTUH
Interpolated Equipment Capacity |  |  | 0 | 63 | #N/A | #N/A | #N/A | #N/A
Excess Latent Capacity Calculation | [5 empty] | #N/A | #N/A
Capacity @ Design Conditions | [5 empty] | #N/A | #N/A | #N/A
Mfg. Equipment Match-Up Adjustment Factor |  |  |  |  | 1 | 1
Altitude Adjustments |  |  |  |  | 1 | 1
Capacity @ Design Conditions |  |  |  |  | #N/A | #N/A | #N/A | #N/A
Equipment Capacity as a % of Design |  |  |  |  | #N/A | #N/A | #N/A
Oversizing Limits |  |  |  |  | 115% |  | 150%
Heat Pump Data (if applicable) |  |  | Capacity @ 47 °F db | Capacity @ 17 °F db | Balance Point | Supplimental Heat Required | Altitude Adjustments
1
[7 empty] | Cap. @ 47 °F db | Cap. @ 17 °F db
[6 empty] | 0 | 0 | 0
Select Furnace or Boiler Option |  |  | Input | Output | Altitude Adjustment | Furnace Capacity | % of Load | Oversing Limits
Furnace Data (if applicable) |  |  | Capacity | Capacity
[5 empty] | 1 | 0 | 0% | 200%
Electric Furnace |  |  | KW Proposed |  | KW Required |  | % of Load | Oversizing Limits
[5 empty] | 0 |  | #DIV/0! | 175%

## Form S-1b
Air Conditioning Contractors of America • Manual S 2nd Edition (2014) Residential Equipment Selection
Project Information |  |  |  |  | Design Information
Name |  |  |  |  | Outdoor Design Temperature - Summer
Address |  |  |  |  | Indoor Design Temperature - Summer
City |  |  |  |  | Indoor Design %RH - Summer
State |  | Zip Code |  |  | Outdoor Design Temperature - Winter
System ID |  |  |  |  | Project Location Elevation |  |  | 1500
Proposed Equipment | System Type | Air-Air, Cooling Only, Single-Speed Compressor, Mild Winter or Latent Load
| Manufacturer |  | Furnace # |  |  |  | AFUE
| Manufacturer |  | AHU/Coil # |  |  |  | SEER
| Manufacturer |  | Condenser # |  |  |  | HSPF
| Manufacturer |  | Package # |  |  |  | Fan Speed | Med
Manual J Load Calculations |  |  |  | Heat | Total | Sensible | Latent | SHR
|  |  |  | Loss | BTUH | BTUH | BTUH
[7 empty] | 0 | #DIV/0!
Enter the listed capacities from the manufacturers cooling performance charts that are equal to the design temperatures here
Out DB per OEM Chart | 0 |  | Design CFM | Return Air | Total | Sensible | Latent | SHR
In DB per OEM Chart | 0 |  |  | (F wb) | BTUH | BTUH | BTUH
Capacity from MFG table |  |  |  | 68 |  |  | 0 | #DIV/0!
Capacity from MFG table |  |  |  | 62 |  |  | 0 | #DIV/0!
Out DB per OEM Chart | 0 |  | Design CFM | Return Air | Total | Sensible | Latent | SHR
In DB per OEM Chart | 0 |  |  | (F wb) | BTUH | BTUH | BTUH
Interpolated Equipment Capacity |  |  | 0 | 63 | 0 | #DIV/0! | #DIV/0! | #DIV/0!
Excess Latent Capacity Calculation | [5 empty] | #DIV/0! | #DIV/0!
Capacity @ Design Conditions | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0!
Mfg. Equipment Match-Up Adjustment Factor |  |  |  |  | 1 | 1
Altitude Adjustments |  |  |  |  | 0.99 | 0.97
Capacity @ Design Conditions |  |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0!
Equipment Capacity as a % of Design |  |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Oversizing Limits |  |  |  |  | 115% |  | 150%
Heat Pump Data (if applicable) |  |  | Capacity @ 47 °F db | Capacity @ 17 °F db | Balance Point | Supplimental Heat Required | Altitude Adjustments
1
[7 empty] | Cap. @ 47 °F db | Cap. @ 17 °F db
[6 empty] | 0 | 0 | 0
Select Furnace or Boiler Option |  |  | Input | Output | Altitude Adjustment | Furnace Capacity | % of Load | Oversing Limits
Furnace Data (if applicable) |  |  | Capacity | Capacity
[5 empty] | 0.84 | 0 | 0% | 200%
Electric Furnace |  |  | KW Proposed |  | KW Required |  | % of Load | Oversizing Limits
[5 empty] | 0 |  | #DIV/0! | 175%

## Form S-1c
Air Conditioning Contractors of America • Manual S 2nd Edition (2014) Residential Equipment Selection
Project Information |  |  |  |  | Design Information
Name |  |  |  |  | Outdoor Design Temperature - Summer
Address |  |  |  |  | Indoor Design Temperature - Summer
City |  |  |  |  | Indoor Design %RH - Summer
State |  | Zip Code |  |  | Outdoor Design Temperature - Winter
System ID |  |  |  |  | Project Location Elevation |  |  | 2500
Proposed Equipment | System Type | Air-Air, Cooling Only, Single-Speed Compressor, Mild Winter or Latent Load
| Manufacturer |  | Furnace # |  |  |  | AFUE
| Manufacturer |  | AHU/Coil # |  |  |  | SEER
| Manufacturer |  | Condenser # |  |  |  | HSPF
| Manufacturer |  | Package # |  |  |  | Fan Speed | Med
Manual J Load Calculations |  |  |  | Heat | Total | Sensible | Latent | SHR
|  |  |  | Loss | BTUH | BTUH | BTUH
[7 empty] | 0 | #DIV/0!
To interpolate capacities, enter the listed capacities from the manufacturers cooling performance charts that are less than the design temperatures here
Out DB per OEM Chart | #N/A |  | Design CFM | Return Air | Total | Sensible | Latent | SHR
In DB per OEM Chart | 0 |  |  | (F wb) | BTUH | BTUH | BTUH
Capacity from MFG table |  |  |  | 63 |  |  | 0 | #DIV/0!
Output from this chart |  |  | 0 | 63 | 0 | 0 | 0 | #DIV/0!
To interpolate capacities, enter the listed capacities from the manufacturers cooling performance charts that are greater than the design temperatures here
Out DB per OEM Chart | #N/A |  | Design CFM | Return Air | Total | Sensible | Latent | SHR
In DB per OEM Chart | 0 |  |  | (F wb) | BTUH | BTUH | BTUH
Capacity from MFG table |  |  | 0 | 63 | 27166.6667 | 23166.6667 | 4000 | 0.85276
Output from this chart |  |  | 0 | 63 | 27166.6667 | 23166.6667 | 4000 | 0.85276
Out DB per OEM Chart | 0 |  | Design CFM | Return Air | Total | Sensible | Latent | SHR
In DB per OEM Chart | 0 |  |  | (F wb) | BTUH | BTUH | BTUH
Interpolated Equipment Capacity |  |  | 0 | 63 | #N/A | #N/A | #N/A | #N/A
Excess Latent Capacity Calculation | [5 empty] | #N/A | #N/A
Capacity @ Design Conditions | [5 empty] | #N/A | #N/A | #N/A
Mfg. Equipment Match-Up Adjustment Factor |  |  |  |  | 1 | 1
Altitude Adjustments |  |  |  |  | 0.98 | 0.94
Capacity @ Design Conditions |  |  |  |  | #N/A | #N/A | #N/A | #N/A
Equipment Capacity as a % of Design |  |  |  |  | #N/A | #N/A | #N/A
Oversizing Limits |  |  |  |  | 115% |  | 150%
Heat Pump Data (if applicable) |  |  | Capacity @ 47 °F db | Capacity @ 17 °F db | Balance Point | Supplimental Heat Required | Altitude Adjustments
1
[7 empty] | Cap. @ 47 °F db | Cap. @ 17 °F db
[6 empty] | 0 | 0 | 0
Select Furnace or Boiler Option |  |  | Input | Output | Altitude Adjustment | Furnace Capacity | % of Load | Oversing Limits
Furnace Data (if applicable) |  |  | Capacity | Capacity
|  |  |  | 0 | 1 | 0 | 0% | 200%
Electric Furnace |  |  | KW Proposed |  | KW Required |  | % of Load | Oversizing Limits
[5 empty] | 0 |  | #DIV/0! | 175%

## Form S-1d
Air Conditioning Contractors of America • Manual S 2nd Edition (2014) Residential Equipment Selection
Project Information |  |  |  |  | Design Information
Name |  |  |  |  | Outdoor Design Temperature - Summer
Address |  |  |  |  | Indoor Design Temperature - Summer
City |  |  |  |  | Indoor Design %RH - Summer
State |  | Zip Code |  |  | Outdoor Design Temperature - Winter
System ID |  |  |  |  | Project Location Elevation |  |  | 3500
Proposed Equipment | System Type | Air-Air, Cooling Only, Single-Speed Compressor, Mild Winter or Latent Load
| Manufacturer |  | Furnace # |  |  |  | AFUE
| Manufacturer |  | AHU/Coil # |  |  |  | SEER
| Manufacturer |  | Condenser # |  |  |  | HSPF
| Manufacturer |  | Package # |  |  |  | Fan Speed | Med
Manual J Load Calculations |  |  |  | Heat | Total | Sensible | Latent | SHR
|  |  |  | Loss | BTUH | BTUH | BTUH
[7 empty] | 0 | #DIV/0!
Enter the listed capacities from the manufacturers cooling performance charts that are equal to 75 (F db) & 63 (F wb) indoor design temperatures here
Out DB per OEM Chart | 0 |  | Design CFM | Return Air | Total | Sensible | Latent | SHR
In DB per OEM Chart | 0 |  |  | (F wb) | BTUH | BTUH | BTUH
Capacity from MFG table |  |  |  | 63 |  |  | 0 | #DIV/0!
Excess Latent Capacity Calculation | [5 empty] | 0 | 0
Capacity @ Design Conditions | [5 empty] | 0 | 0 | #DIV/0!
Mfg. Equipment Match-Up Adjustment Factor |  |  |  |  | 1 | 1
Altitude Adjustments |  |  |  |  | 0.98 | 0.91
Capacity @ Design Conditions |  |  |  |  | 0 | 0 | 0 | #DIV/0!
Equipment Capacity as a % of Design |  |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
Oversizing Limits |  |  |  |  | 115% |  | 150%
Heat Pump Data (if applicable) |  |  | Capacity @ 47 °F db | Capacity @ 17 °F db | Balance Point | Supplimental Heat Required | Altitude Adjustments
1
[7 empty] | Cap. @ 47 °F db | Cap. @ 17 °F db
[6 empty] | 0 | 0 | 0
Select Furnace or Boiler Option |  |  | Input | Output | Altitude Adjustment | Furnace Capacity | % of Load | Oversing Limits
Furnace Data (if applicable) |  |  | Capacity | Capacity
|  |  |  | 0 | 1 | 0 | 0% | 200%
Electric Furnace |  |  | KW Proposed |  | KW Required |  | % of Load | Oversizing Limits
[5 empty] | 0 |  | #DIV/0! | 175%

## Data (hidden)
SHR | TD | -15% | Not Acceptable | [8 empty] | <select> | 0 | 0
0 | 21 | 15% | Acceptable | [8 empty] | Air-Air, Cooling Only, Single-Speed Compressor, Mild Winter or Latent Load | 1.15 | 1.5
0.8 | 19 | 15.01% | Not Acceptable | [8 empty] | Air-Air, Heat Pump, Single-Speed Compressor, Mild Winter or Latent Load | 1.15 | 1.5
0.85 | 17 | [10 empty] | Air-Air, Cooling Only, Multi-Speed Compressor, Mild Winter or Latent Load | 1.2 | 1.5
Calculated | #DIV/0! | [10 empty] | Air-Air, Heat Pump, Multi-Speed Compressor, Mild Winter or Latent Load | 1.2 | 1.5
[12 empty] | Air-Air, Cooling Only, Variable Speed Compressor, Mild Winter or Latent Load | 1.3 | 1.5
45 | 62 | [10 empty] | Air-Air, Heat Pump, Variable Speed Compressor, Mild Winter or Latent Load | 1.3 | 1.5
50 | 63 | [7 empty] | Sys 1 |  |  | Air-Air, Cooling Only, Single-Speed Compressor, Cold Winter or No Latent Load | #DIV/0! | 1.5
55 | 64 | 0 |  | 75 | 75 |  |  |  | 0 |  |  | Air-Air, Heat Pump, Single-Speed Compressor, Cold Winter or No Latent Load | #DIV/0! | 1.5
|  | 0 |  | 76 | 75 |  |  |  | 0 |  |  | Air-Air, Cooling Only, Multi-Speed Compressor, Cold Winter or No Latent Load | #DIV/0! | 1.5
|  | 0 |  | 77 | 75 |  |  |  | 0 |  |  | Air-Air, Heat Pump, Multi-Speed Compressor, Cold Winter or No Latent Load | #DIV/0! | 1.5
|  | 17 |  | 78 | 75 |  |  |  | 17 |  |  | Air-Air, Cooling Only, Variable Speed Compressor, Cold Winter or No Latent Load | #DIV/0! | 1.5
|  | 0 |  | 79 | 75 |  |  |  | 0 |  |  | Air-Air, Heat Pump, Variable Speed Compressor, Cold Winter or No Latent Load | #DIV/0! | 1.5
Capacity @ Winter Design | 0 | 0 |  | 80 | 75 | Capacity @ Winter Design | 0 |  | 0 |  |  | Furnace Heating Only | #DIV/0! | 1.5
Total Heat loss @ Winter Design | 0 | 0 |  | 81 | 75 | Total Heat loss @ Winter Design | 0 |  | 0 |  |  | Boiler Heating Only | #DIV/0! | 1.5 | 1.4
Electric Heat required |  | 0 | KW | 82 | 75 | Electric Heat required |  |  | 0
|  |  |  | 83 | 75
Altitude Adjustment |  |  |  | 84 | 75 | [6 empty] | <select> | 0
0 | 1 | Yes |  | 85 | 85 | [6 empty] | Furnace Data (if applicable) | 2
1000 | 0.98 | No |  | 86 | 85 | [6 empty] | Furnace Data, heating only (if applicable) | 1.4
2000 | 0.97 |  |  | 87 | 85 | [6 empty] | Boiler Data, heating only (if applicable) | 1.4
3000 | 0.95 | 57 |  | 88 | 85
4000 | 0.94 | 62 |  | 89 | 85
5000 | 0.92 | 67 |  | 90 | 85 |  | Derating Capacity Due to Elevation
6000 | 0.9 | 72 |  | 91 | 85 |  |  | Furnaces | Air/Air Refrigerant-based
7000 | 0.89 |  |  | 92 | 85 |  | Altitude | Total | Total Wet | Sensible Wet | Total Dry
8000 | 0.87 |  |  | 93 | 85 |  | 0 | 1 | 1 | 1 | 1
9000 | 0.86 |  |  | 94 | 85 |  | 1000 | 0.96 | 0.99 | 0.97 | 0.98
10000 | 0.84 |  |  | 95 | 95 |  | 2000 | 0.92 | 0.98 | 0.94 | 0.97
11000 | 0.82 |  |  | 96 | 95 |  | 3000 | 0.88 | 0.98 | 0.91 | 0.95
12000 | 0.81 |  |  | 97 | 95 |  | 4000 | 0.84 | 0.97 | 0.88 | 0.94
|  |  |  | 98 | 95 |  | 5000 | 0.8 | 0.96 | 0.85 | 0.92
|  |  |  | 99 | 95 |  | 6000 | 0.76 | 0.95 | 0.82 | 0.9
|  |  |  | 100 | 95 |  | 7000 | 0.72 | 0.94 | 0.8 | 0.89
|  |  |  | 101 | 95 |  | 8000 | 0.68 | 0.94 | 0.77 | 0.87
|  |  |  | 102 | 95 |  | 9000 | 0.64 | 0.93 | 0.74 | 0.86
|  |  |  | 103 | 95 |  | 10000 | 0.6 | 0.92 | 0.71 | 0.84
|  |  |  | 104 | 95 |  | 11000 | 0.56 | 0.91 | 0.68 | 0.82
|  |  |  | 105 | 105 |  | 12000 | 0.52 | 0.9 | 0.65 | 0.81
|  |  |  | 106 | 105
|  |  |  | 107 | 105 |  |  | 1 | 1 | 1 | 1
|  |  |  | 108 | 105 |  |  | 0.96 | 0.99 | 0.97 | 0.98
|  |  |  | 109 | 105 |  |  | 0.92 | 0.98 | 0.94 | 0.97
|  |  |  | 110 | 105 |  |  | 0.88 | 0.98 | 0.91 | 0.95
|  |  |  | 111 | 105
|  |  |  | 112 | 105
|  |  |  | 113 | 105
|  |  |  | 114 | 105
|  |  |  | 115 | 115
|  |  |  | 116 | 115
|  |  |  | 117 | 115
|  |  |  | 118 | 115
|  |  |  | 119 | 115
|  |  |  | 120 | 115
|  |  |  | 121 | 115
|  |  |  | 122 | 115
|  |  |  | 123 | 115
|  |  |  | 124 | 115
|  |  |  | 125 | 125
|  |  |  | 126 | 125
|  |  |  | 127 | 125
|  |  |  | 128 | 125
|  |  |  | 129 | 125
|  |  |  | 130 | 125
|  |  |  | 131 | 125
|  |  |  | 132 | 125
|  |  |  | 133 | 125
|  |  |  | 134 | 125

## System3 (hidden)
Equipment Selection Analysis via Manual-S Protocols
| Completed by | #REF! |  |  |  |  | Form developed by:
#REF!
| Project Information |  |  |  |  | Design Information
| Name | #REF! |  |  |  | Outdoor Design Temperature - Summer |  |  | #REF!
| Address | #REF! |  |  |  | Indoor Design Temperature - Summer |  |  | #REF!
| City | #REF! |  |  |  | Indoor Design %RH - Summer |  |  | #REF!
| State | #REF! | Zip Code | #REF! |  | Outdoor Design Temperature - Winter |  |  | #REF!
| Permit # | #REF! |  |  |  | Project Location Elevation |  |  | #REF!
| System Name | #REF! |  |  | System Type | #REF!
| Proposed Equipment | Manufacturer |  | Furnace # |  |  |  | AFUE
|  | Manufacturer |  | AHU/Coil # |  |  |  | SEER
|  | Manufacturer |  | Condenser # |  |  |  | HSPF
|  | Manufacturer |  | Package # |  |  |  | Equip. Match-Up Adjust Factor
[8 empty] | Total | Sensible
[8 empty] | 1 | 1
| Manual J Load | Heat | Total | Sensible | Latent | SHR | Chart Indoor Dry Bulb | Is Data Available for 75DB/63WB? | Capacity Adj 1000cfm/deg
|  | Loss | BTUH | BTUH | BTUH
|  | #REF! | #REF! | #REF! | #REF! | #REF! | 80 | No
Capacity <= Design Temp | Out DB per Chart | #REF! |  | CFM | Return Air | Total | Sensible | Latent | SHR
| In DB per Chart | 80 |  |  | (F wb) | BTUH | BTUH | BTUH
| Capacity from MFG table | [6 empty] | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| Capacity from MFG table |  |  |  | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Modified for Design DB | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0!
| Capacity from MFG table | [6 empty] | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| N/A |  |  |  | 63 |  |  | 0 | #DIV/0!
| Output from this chart |  |  | 0 | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Capacity >= Design Temp | Out DB per Chart | #REF! |  | CFM | Return Air | Total | Sensible | Latent | SHR
| In DB per Chart | 80 |  |  | (F wb) | BTUH | BTUH | BTUH
| Capacity from MFG table |  |  | 0 | 0 |  |  | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| Capacity from MFG table |  |  |  | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Modified for Design DB | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0!
| Capacity from MFG table |  |  |  | 0 |  |  | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| N/A |  |  |  | 63 |  |  | 0 | #DIV/0!
| Output from this chart |  |  | 0 | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Capaicty @ Design | Out DB | #REF! |  | CFM | Return Air | Total | Sensible | Latent | SHR
| In DB | #REF! |  |  | (F wb) | BTUH | BTUH | BTUH
| Interpolated Equipment Capacity |  |  | 0 | 63 | #REF! | #REF! | #REF! | #REF!
| Excess Latent Capacity Calculation | [5 empty] | #REF! | #REF!
| Capacity @ Design Conditions | [5 empty] | #REF! | #REF! | #REF!
| Equipment Capacity as a % of Design |  |  |  |  | #REF! | #REF! | #REF!
| COOLING CAPACITY AT DESIGN CONDITIONS |  |  | CFM | Return Air WB | Total Capacity | Sensible | Latent | SHR | Alt Total | Alt Sensible
|  |  |  | 0 | 63 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Heat Pump Data (if applicable) |  |  | Capacity | Capacity | Balance | Supplimental Heat Required | Alt. Adj. Cap. @ 47 °F db | Alt. Adj. Cap. @ 17 °F db | Alt. Factor
|  |  |  | @ 47 °F db | @ 17 °F db | Point
[7 empty] | 0 | #REF! | #REF! | #REF!
| Furnace Data (if applicable) |  |  | Input | Output | AFUE | % of Load | Next Size Down? (-20kbtu input) |  | Alt. Factor
|  |  |  | Capacity | Capacity
[5 empty] | #REF! | 0 |  | N/A |  | #REF!
#REF!
Note on J7: To change this field, go to the Set-Up Data Tab.
Note on J10: To change this field, go to the Set-Up Data Tab.
Note on G13: To change this field, go to the Set-Up Data Tab.
Note on I20: These are provided to adjust the capacity for a variety of equipment match-ups. These are typically found beneath the detailed cooling capacity data chart.
Note on J20: These are provided to adjust the capacity for a variety of equipment match-ups. These are typically found beneath the detailed cooling capacity data chart.
Note on E24: Make sure you're NOT using the RSM load from Wrightsoft reports here. You'll want to use the RAW load data instead.
Note on I24: Many OEM's don't provide capacity data at 75 drybulb. If your's does, then choose YES here.
Note on J24: Enter the adjustment # from footnotes here, if 75/63 data is not available.
Note on E28: Input the CFM value you'll be using to describe the capacity of the equipment. For 2-stage equipment, this would be the HIGH stage.
Note on F28: This temperature should be WARMER than 63 degrees.
Note on G28: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on H28: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on F32: This temperature should be COOLER than 63 degrees.
Note on G32: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on H32: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on G39: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on H39: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on G43: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on H43: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on E60: Enter capacity from OEM data. Often called "high temp" capacity.
Note on F60: Enter capacity from OEM data. Often called "low temp" capacity.

## System4 (hidden)
Equipment Selection Analysis via Manual-S Protocols
| Completed by | #REF! |  |  |  |  | Form developed by:
#REF!
| Project Information |  |  |  |  | Design Information
| Name | #REF! |  |  |  | Outdoor Design Temperature - Summer |  |  | #REF!
| Address | #REF! |  |  |  | Indoor Design Temperature - Summer |  |  | #REF!
| City | #REF! |  |  |  | Indoor Design %RH - Summer |  |  | #REF!
| State | #REF! | Zip Code | #REF! |  | Outdoor Design Temperature - Winter |  |  | #REF!
| Permit # | #REF! |  |  |  | Project Location Elevation |  |  | #REF!
| System Name | #REF! |  |  | System Type | #REF!
| Proposed Equipment | Manufacturer |  | Furnace # |  |  |  | AFUE
|  | Manufacturer |  | AHU/Coil # |  |  |  | SEER
|  | Manufacturer |  | Condenser # |  |  |  | HSPF
|  | Manufacturer |  | Package # |  |  |  | Equip. Match-Up Adjust Factor
[8 empty] | Total | Sensible
[8 empty] | 1 | 1
| Manual J Load | Heat | Total | Sensible | Latent | SHR | Chart Indoor Dry Bulb | Is Data Available for 75DB/63WB? | Capacity Adj 1000cfm/deg
|  | Loss | BTUH | BTUH | BTUH
|  | #REF! | #REF! | #REF! | #REF! | #REF! | 80 | No
Capacity <= Design Temp | Out DB per Chart | #REF! |  | CFM | Return Air | Total | Sensible | Latent | SHR
| In DB per Chart | 80 |  |  | (F wb) | BTUH | BTUH | BTUH
| Capacity from MFG table | [6 empty] | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| Capacity from MFG table |  |  |  | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Modified for Design DB | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0!
| Capacity from MFG table | [6 empty] | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| N/A |  |  |  | 63 |  |  | 0 | #DIV/0!
| Output from this chart |  |  | 0 | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Capacity >= Design Temp | Out DB per Chart | #REF! |  | CFM | Return Air | Total | Sensible | Latent | SHR
| In DB per Chart | 80 |  |  | (F wb) | BTUH | BTUH | BTUH
| Capacity from MFG table |  |  | 0 | 0 |  |  | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| Capacity from MFG table |  |  |  | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Modified for Design DB | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0!
| Capacity from MFG table |  |  |  | 0 |  |  | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| N/A |  |  |  | 63 |  |  | 0 | #DIV/0!
| Output from this chart |  |  | 0 | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Capaicty @ Design | Out DB | #REF! |  | CFM | Return Air | Total | Sensible | Latent | SHR
| In DB | #REF! |  |  | (F wb) | BTUH | BTUH | BTUH
| Interpolated Equipment Capacity |  |  | 0 | 63 | #REF! | #REF! | #REF! | #REF!
| Excess Latent Capacity Calculation | [5 empty] | #REF! | #REF!
| Capacity @ Design Conditions | [5 empty] | #REF! | #REF! | #REF!
| Equipment Capacity as a % of Design |  |  |  |  | #REF! | #REF! | #REF!
| COOLING CAPACITY AT DESIGN CONDITIONS |  |  | CFM | Return Air WB | Total Capacity | Sensible | Latent | SHR | Alt Total | Alt Sensible
|  |  |  | 0 | 63 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Heat Pump Data (if applicable) |  |  | Capacity | Capacity | Balance | Supplimental Heat Required | Alt. Adj. Cap. @ 47 °F db | Alt. Adj. Cap. @ 17 °F db | Alt. Factor
|  |  |  | @ 47 °F db | @ 17 °F db | Point
[7 empty] | 0 | #REF! | #REF! | #REF!
| Furnace Data (if applicable) |  |  | Input | Output | AFUE | % of Load | Next Size Down? (-20kbtu input) |  | Alt. Factor
|  |  |  | Capacity | Capacity
[5 empty] | #REF! | 0 |  | N/A |  | #REF!
For instructional video, visit: HomeEnergyPartners.com/Manual-S
Note on J7: To change this field, go to the Set-Up Data Tab.
Note on J10: To change this field, go to the Set-Up Data Tab.
Note on G13: To change this field, go to the Set-Up Data Tab.
Note on I20: These are provided to adjust the capacity for a variety of equipment match-ups. These are typically found beneath the detailed cooling capacity data chart.
Note on J20: These are provided to adjust the capacity for a variety of equipment match-ups. These are typically found beneath the detailed cooling capacity data chart.
Note on E24: Make sure you're NOT using the RSM load from Wrightsoft reports here. You'll want to use the RAW load data instead.
Note on I24: Many OEM's don't provide capacity data at 75 drybulb. If your's does, then choose YES here.
Note on J24: Enter the adjustment # from footnotes here, if 75/63 data is not available.
Note on E28: Input the CFM value you'll be using to describe the capacity of the equipment. For 2-stage equipment, this would be the HIGH stage.
Note on F28: This temperature should be WARMER than 63 degrees.
Note on G28: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on H28: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on F32: This temperature should be COOLER than 63 degrees.
Note on G32: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on H32: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on G39: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on H39: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on G43: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on H43: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on E60: Enter capacity from OEM data. Often called "high temp" capacity.
Note on F60: Enter capacity from OEM data. Often called "low temp" capacity.

## System5 (hidden)
Equipment Selection Analysis via Manual-S Protocols
| Completed by | #REF! |  |  |  |  | Form developed by:
#REF!
| Project Information |  |  |  |  | Design Information
| Name | #REF! |  |  |  | Outdoor Design Temperature - Summer |  |  | #REF!
| Address | #REF! |  |  |  | Indoor Design Temperature - Summer |  |  | #REF!
| City | #REF! |  |  |  | Indoor Design %RH - Summer |  |  | #REF!
| State | #REF! | Zip Code | #REF! |  | Outdoor Design Temperature - Winter |  |  | #REF!
| Permit # | #REF! |  |  |  | Project Location Elevation |  |  | #REF!
| System Name | #REF! |  |  | System Type | #REF!
| Proposed Equipment | Manufacturer |  | Furnace # |  |  |  | AFUE
|  | Manufacturer |  | AHU/Coil # |  |  |  | SEER
|  | Manufacturer |  | Condenser # |  |  |  | HSPF
|  | Manufacturer |  | Package # |  |  |  | Equip. Match-Up Adjust Factor
[8 empty] | Total | Sensible
[8 empty] | 1 | 1
| Manual J Load | Heat | Total | Sensible | Latent | SHR | Chart Indoor Dry Bulb | Is Data Available for 75DB/63WB? | Capacity Adj 1000cfm/deg
|  | Loss | BTUH | BTUH | BTUH
|  | #REF! | #REF! | #REF! | #REF! | #REF! | 80 | No
Capacity <= Design Temp | Out DB per Chart | #REF! |  | CFM | Return Air | Total | Sensible | Latent | SHR
| In DB per Chart | 80 |  |  | (F wb) | BTUH | BTUH | BTUH
| Capacity from MFG table | [6 empty] | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| Capacity from MFG table |  |  |  | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Modified for Design DB | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0!
| Capacity from MFG table | [6 empty] | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| N/A |  |  |  | 63 |  |  | 0 | #DIV/0!
| Output from this chart |  |  | 0 | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Capacity >= Design Temp | Out DB per Chart | #REF! |  | CFM | Return Air | Total | Sensible | Latent | SHR
| In DB per Chart | 80 |  |  | (F wb) | BTUH | BTUH | BTUH
| Capacity from MFG table |  |  | 0 | 0 |  |  | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| Capacity from MFG table |  |  |  | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Modified for Design DB | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0!
| Capacity from MFG table |  |  |  | 0 |  |  | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| N/A |  |  |  | 63 |  |  | 0 | #DIV/0!
| Output from this chart |  |  | 0 | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Capaicty @ Design | Out DB | #REF! |  | CFM | Return Air | Total | Sensible | Latent | SHR
| In DB | #REF! |  |  | (F wb) | BTUH | BTUH | BTUH
| Interpolated Equipment Capacity |  |  | 0 | 63 | #REF! | #REF! | #REF! | #REF!
| Excess Latent Capacity Calculation | [5 empty] | #REF! | #REF!
| Capacity @ Design Conditions | [5 empty] | #REF! | #REF! | #REF!
| Equipment Capacity as a % of Design |  |  |  |  | #REF! | #REF! | #REF!
| COOLING CAPACITY AT DESIGN CONDITIONS |  |  | CFM | Return Air WB | Total Capacity | Sensible | Latent | SHR | Alt Total | Alt Sensible
|  |  |  | 0 | 63 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Heat Pump Data (if applicable) |  |  | Capacity | Capacity | Balance | Supplimental Heat Required | Alt. Adj. Cap. @ 47 °F db | Alt. Adj. Cap. @ 17 °F db | Alt. Factor
|  |  |  | @ 47 °F db | @ 17 °F db | Point
[7 empty] | Boiler Data, heating only (if applicable) | #REF! | #REF! | #REF!
| Furnace Data (if applicable) |  |  | Input | Output | AFUE | % of Load | Next Size Down? (-20kbtu input) |  | Alt. Factor
|  |  |  | Capacity | Capacity
[5 empty] | #REF! | 0 |  | N/A |  | #REF!
For instructional video, visit: HomeEnergyPartners.com/Manual-S
Note on J7: To change this field, go to the Set-Up Data Tab.
Note on J10: To change this field, go to the Set-Up Data Tab.
Note on G13: To change this field, go to the Set-Up Data Tab.
Note on I20: These are provided to adjust the capacity for a variety of equipment match-ups. These are typically found beneath the detailed cooling capacity data chart.
Note on J20: These are provided to adjust the capacity for a variety of equipment match-ups. These are typically found beneath the detailed cooling capacity data chart.
Note on E24: Make sure you're NOT using the RSM load from Wrightsoft reports here. You'll want to use the RAW load data instead.
Note on I24: Many OEM's don't provide capacity data at 75 drybulb. If your's does, then choose YES here.
Note on J24: Enter the adjustment # from footnotes here, if 75/63 data is not available.
Note on E28: Input the CFM value you'll be using to describe the capacity of the equipment. For 2-stage equipment, this would be the HIGH stage.
Note on F28: This temperature should be WARMER than 63 degrees.
Note on G28: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on H28: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on F32: This temperature should be COOLER than 63 degrees.
Note on G32: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on H32: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on G39: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on H39: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on G43: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on H43: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on E60: Enter capacity from OEM data. Often called "high temp" capacity.
Note on F60: Enter capacity from OEM data. Often called "low temp" capacity.

## System6 (hidden)
Equipment Selection Analysis via Manual-S Protocols
| Completed by | #REF! |  |  |  |  | Form developed by:
#REF!
| Project Information |  |  |  |  | Design Information
| Name | #REF! |  |  |  | Outdoor Design Temperature - Summer |  |  | #REF!
| Address | #REF! |  |  |  | Indoor Design Temperature - Summer |  |  | #REF!
| City | #REF! |  |  |  | Indoor Design %RH - Summer |  |  | #REF!
| State | #REF! | Zip Code | #REF! |  | Outdoor Design Temperature - Winter |  |  | #REF!
| Permit # | #REF! |  |  |  | Project Location Elevation |  |  | #REF!
| System Name | #REF! |  |  | System Type | #REF!
| Proposed Equipment | Manufacturer |  | Furnace # |  |  |  | AFUE | 98
|  | Manufacturer |  | AHU/Coil # |  |  |  | SEER
|  | Manufacturer |  | Condenser # |  |  |  | HSPF
|  | Manufacturer |  | Package # |  |  |  | Equip. Match-Up Adjust Factor
[8 empty] | Total | Sensible
[8 empty] | 1 | 1
| Manual J Load | Heat | Total | Sensible | Latent | SHR | Chart Indoor Dry Bulb | Is Data Available for 75DB/63WB? | Capacity Adj 1000cfm/deg
|  | Loss | BTUH | BTUH | BTUH
|  | #REF! | #REF! | #REF! | #REF! | #REF! | 80 | No
Capacity <= Design Temp | Out DB per Chart | #REF! |  | CFM | Return Air | Total | Sensible | Latent | SHR
| In DB per Chart | 80 |  |  | (F wb) | BTUH | BTUH | BTUH
| Capacity from MFG table | [6 empty] | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| Capacity from MFG table |  |  |  | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Modified for Design DB | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0!
| Capacity from MFG table | [6 empty] | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| N/A |  |  |  | 63 |  |  | 0 | #DIV/0!
| Output from this chart |  |  | 0 | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Capacity >= Design Temp | Out DB per Chart | #REF! |  | CFM | Return Air | Total | Sensible | Latent | SHR
| In DB per Chart | 80 |  |  | (F wb) | BTUH | BTUH | BTUH
| Capacity from MFG table |  |  | 0 | 0 |  |  | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| Capacity from MFG table |  |  |  | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Modified for Design DB | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0!
| Capacity from MFG table |  |  |  | 0 |  |  | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| N/A |  |  |  | 63 |  |  | 0 | #DIV/0!
| Output from this chart |  |  | 0 | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Capaicty @ Design | Out DB | #REF! |  | CFM | Return Air | Total | Sensible | Latent | SHR
| In DB | #REF! |  |  | (F wb) | BTUH | BTUH | BTUH
| Interpolated Equipment Capacity |  |  | 0 | 63 | #REF! | #REF! | #REF! | #REF!
| Excess Latent Capacity Calculation | [5 empty] | #REF! | #REF!
| Capacity @ Design Conditions | [5 empty] | #REF! | #REF! | #REF!
| Equipment Capacity as a % of Design |  |  |  |  | #REF! | #REF! | #REF!
| COOLING CAPACITY AT DESIGN CONDITIONS |  |  | CFM | Return Air WB | Total Capacity | Sensible | Latent | SHR | Alt Total | Alt Sensible
|  |  |  | 0 | 63 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Heat Pump Data (if applicable) |  |  | Capacity | Capacity | Balance | Supplimental Heat Required | Alt. Adj. Cap. @ 47 °F db | Alt. Adj. Cap. @ 17 °F db | Alt. Factor
|  |  |  | @ 47 °F db | @ 17 °F db | Point
[7 empty] | 1.4 | #REF! | #REF! | #REF!
| Furnace Data (if applicable) |  |  | Input | Output | AFUE | % of Load | Next Size Down? (-20kbtu input) |  | Alt. Factor
|  |  |  | Capacity | Capacity
[5 empty] | #REF! | 98 |  | N/A |  | #REF!
For instructional video, visit: HomeEnergyPartners.com/Manual-S
Note on J7: To change this field, go to the Set-Up Data Tab.
Note on J10: To change this field, go to the Set-Up Data Tab.
Note on G13: To change this field, go to the Set-Up Data Tab.
Note on I20: These are provided to adjust the capacity for a variety of equipment match-ups. These are typically found beneath the detailed cooling capacity data chart.
Note on J20: These are provided to adjust the capacity for a variety of equipment match-ups. These are typically found beneath the detailed cooling capacity data chart.
Note on E24: Make sure you're NOT using the RSM load from Wrightsoft reports here. You'll want to use the RAW load data instead.
Note on I24: Many OEM's don't provide capacity data at 75 drybulb. If your's does, then choose YES here.
Note on J24: Enter the adjustment # from footnotes here, if 75/63 data is not available.
Note on E28: Input the CFM value you'll be using to describe the capacity of the equipment. For 2-stage equipment, this would be the HIGH stage.
Note on F28: This temperature should be WARMER than 63 degrees.
Note on G28: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on H28: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on F32: This temperature should be COOLER than 63 degrees.
Note on G32: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on H32: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on G39: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on H39: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on G43: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on H43: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on E60: Enter capacity from OEM data. Often called "high temp" capacity.
Note on F60: Enter capacity from OEM data. Often called "low temp" capacity.

## System7 (hidden)
Equipment Selection Analysis via Manual-S Protocols
| Completed by | #REF! |  |  |  |  | Form developed by:
#REF!
| Project Information |  |  |  |  | Design Information
| Name | #REF! |  |  |  | Outdoor Design Temperature - Summer |  |  | #REF!
| Address | #REF! |  |  |  | Indoor Design Temperature - Summer |  |  | #REF!
| City | #REF! |  |  |  | Indoor Design %RH - Summer |  |  | #REF!
| State | #REF! | Zip Code | #REF! |  | Outdoor Design Temperature - Winter |  |  | #REF!
| Permit # | #REF! |  |  |  | Project Location Elevation |  |  | #REF!
| System Name | #REF! |  |  | System Type | #REF!
| Proposed Equipment | Manufacturer |  | Furnace # |  |  |  | AFUE
|  | Manufacturer |  | AHU/Coil # |  |  |  | SEER
|  | Manufacturer |  | Condenser # |  |  |  | HSPF
|  | Manufacturer |  | Package # |  |  |  | Equip. Match-Up Adjust Factor
[8 empty] | Total | Sensible
[8 empty] | 1 | 1
| Manual J Load | Heat | Total | Sensible | Latent | SHR | Chart Indoor Dry Bulb | Is Data Available for 75DB/63WB? | Capacity Adj 1000cfm/deg
|  | Loss | BTUH | BTUH | BTUH
|  | #REF! | #REF! | #REF! | #REF! | #REF! | 80 | No
Capacity <= Design Temp | Out DB per Chart | #REF! |  | CFM | Return Air | Total | Sensible | Latent | SHR
| In DB per Chart | 80 |  |  | (F wb) | BTUH | BTUH | BTUH
| Capacity from MFG table | [6 empty] | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| Capacity from MFG table |  |  |  | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Modified for Design DB | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0!
| Capacity from MFG table | [6 empty] | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| N/A |  |  |  | 63 |  |  | 0 | #DIV/0!
| Output from this chart |  |  | 0 | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Capacity >= Design Temp | Out DB per Chart | #REF! |  | CFM | Return Air | Total | Sensible | Latent | SHR
| In DB per Chart | 80 |  |  | (F wb) | BTUH | BTUH | BTUH
| Capacity from MFG table |  |  | 0 | 0 |  |  | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| Capacity from MFG table |  |  |  | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Modified for Design DB | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0!
| Capacity from MFG table |  |  |  | 0 |  |  | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| N/A |  |  |  | 63 |  |  | 0 | #DIV/0!
| Output from this chart |  |  | 0 | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Capaicty @ Design | Out DB | #REF! |  | CFM | Return Air | Total | Sensible | Latent | SHR
| In DB | #REF! |  |  | (F wb) | BTUH | BTUH | BTUH
| Interpolated Equipment Capacity |  |  | 0 | 63 | #REF! | #REF! | #REF! | #REF!
| Excess Latent Capacity Calculation | [5 empty] | #REF! | #REF!
| Capacity @ Design Conditions | [5 empty] | #REF! | #REF! | #REF!
| Equipment Capacity as a % of Design |  |  |  |  | #REF! | #REF! | #REF!
| COOLING CAPACITY AT DESIGN CONDITIONS |  |  | CFM | Return Air WB | Total Capacity | Sensible | Latent | SHR | Alt Total | Alt Sensible
|  |  |  | 0 | 63 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Heat Pump Data (if applicable) |  |  | Capacity | Capacity | Balance | Supplimental Heat Required | Alt. Adj. Cap. @ 47 °F db | Alt. Adj. Cap. @ 17 °F db | Alt. Factor
|  |  |  | @ 47 °F db | @ 17 °F db | Point
[7 empty] | 0 | #REF! | #REF! | #REF!
| Furnace Data (if applicable) |  |  | Input | Output | AFUE | % of Load | Next Size Down? (-20kbtu input) |  | Alt. Factor
|  |  |  | Capacity | Capacity
[5 empty] | #REF! | 0 |  | N/A |  | #REF!
For instructional video, visit: HomeEnergyPartners.com/Manual-S
Note on J7: To change this field, go to the Set-Up Data Tab.
Note on J10: To change this field, go to the Set-Up Data Tab.
Note on G13: To change this field, go to the Set-Up Data Tab.
Note on I20: These are provided to adjust the capacity for a variety of equipment match-ups. These are typically found beneath the detailed cooling capacity data chart.
Note on J20: These are provided to adjust the capacity for a variety of equipment match-ups. These are typically found beneath the detailed cooling capacity data chart.
Note on E24: Make sure you're NOT using the RSM load from Wrightsoft reports here. You'll want to use the RAW load data instead.
Note on I24: Many OEM's don't provide capacity data at 75 drybulb. If your's does, then choose YES here.
Note on J24: Enter the adjustment # from footnotes here, if 75/63 data is not available.
Note on E28: Input the CFM value you'll be using to describe the capacity of the equipment. For 2-stage equipment, this would be the HIGH stage.
Note on F28: This temperature should be WARMER than 63 degrees.
Note on G28: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on H28: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on F32: This temperature should be COOLER than 63 degrees.
Note on G32: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on H32: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on G39: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on H39: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on G43: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on H43: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on E60: Enter capacity from OEM data. Often called "high temp" capacity.
Note on F60: Enter capacity from OEM data. Often called "low temp" capacity.

## System8 (hidden)
Equipment Selection Analysis via Manual-S Protocols
| Completed by | #REF! |  |  |  |  | Form developed by:
#REF!
| Project Information |  |  |  |  | Design Information
| Name | #REF! |  |  |  | Outdoor Design Temperature - Summer |  |  | #REF!
| Address | #REF! |  |  |  | Indoor Design Temperature - Summer |  |  | #REF!
| City | #REF! |  |  |  | Indoor Design %RH - Summer |  |  | #REF!
| State | #REF! | Zip Code | #REF! |  | Outdoor Design Temperature - Winter |  |  | #REF!
| Permit # | #REF! |  |  |  | Project Location Elevation |  |  | #REF!
| System Name | #REF! |  |  | System Type | #REF!
| Proposed Equipment | Manufacturer |  | Furnace # |  |  |  | AFUE
|  | Manufacturer |  | AHU/Coil # |  |  |  | SEER
|  | Manufacturer |  | Condenser # |  |  |  | HSPF
|  | Manufacturer |  | Package # |  |  |  | Equip. Match-Up Adjust Factor
[8 empty] | Total | Sensible
[8 empty] | 1 | 1
| Manual J Load | Heat | Total | Sensible | Latent | SHR | Chart Indoor Dry Bulb | Is Data Available for 75DB/63WB? | Capacity Adj 1000cfm/deg
|  | Loss | BTUH | BTUH | BTUH
|  | #REF! | #REF! | #REF! | #REF! | #REF! | 80 | No
Capacity <= Design Temp | Out DB per Chart | #REF! |  | CFM | Return Air | Total | Sensible | Latent | SHR
| In DB per Chart | 80 |  |  | (F wb) | BTUH | BTUH | BTUH
| Capacity from MFG table | [6 empty] | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| Capacity from MFG table |  |  |  | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Modified for Design DB | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0!
| Capacity from MFG table | [6 empty] | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| N/A |  |  |  | 63 |  |  | 0 | #DIV/0!
| Output from this chart |  |  | 0 | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Capacity >= Design Temp | Out DB per Chart | #REF! |  | CFM | Return Air | Total | Sensible | Latent | SHR
| In DB per Chart | 80 |  |  | (F wb) | BTUH | BTUH | BTUH
| Capacity from MFG table |  |  | 0 | 0 |  |  | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| Capacity from MFG table |  |  |  | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Modified for Design DB | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0!
| Capacity from MFG table |  |  |  | 0 |  |  | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| N/A |  |  |  | 63 |  |  | 0 | #DIV/0!
| Output from this chart |  |  | 0 | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Capaicty @ Design | Out DB | #REF! |  | CFM | Return Air | Total | Sensible | Latent | SHR
| In DB | #REF! |  |  | (F wb) | BTUH | BTUH | BTUH
| Interpolated Equipment Capacity |  |  | 0 | 63 | #REF! | #REF! | #REF! | #REF!
| Excess Latent Capacity Calculation | [5 empty] | #REF! | #REF!
| Capacity @ Design Conditions | [5 empty] | #REF! | #REF! | #REF!
| Equipment Capacity as a % of Design |  |  |  |  | #REF! | #REF! | #REF!
| COOLING CAPACITY AT DESIGN CONDITIONS |  |  | CFM | Return Air WB | Total Capacity | Sensible | Latent | SHR | Alt Total | Alt Sensible
|  |  |  | 0 | 63 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Heat Pump Data (if applicable) |  |  | Capacity | Capacity | Balance | Supplimental Heat Required | Alt. Adj. Cap. @ 47 °F db | Alt. Adj. Cap. @ 17 °F db | Alt. Factor
|  |  |  | @ 47 °F db | @ 17 °F db | Point
[7 empty] | 0 | #REF! | #REF! | #REF!
| Furnace Data (if applicable) |  |  | Input | Output | AFUE | % of Load | Next Size Down? (-20kbtu input) |  | Alt. Factor
|  |  |  | Capacity | Capacity
[5 empty] | #REF! | 0 |  | N/A |  | #REF!
For instructional video, visit: HomeEnergyPartners.com/Manual-S
Note on J7: To change this field, go to the Set-Up Data Tab.
Note on J10: To change this field, go to the Set-Up Data Tab.
Note on G13: To change this field, go to the Set-Up Data Tab.
Note on I20: These are provided to adjust the capacity for a variety of equipment match-ups. These are typically found beneath the detailed cooling capacity data chart.
Note on J20: These are provided to adjust the capacity for a variety of equipment match-ups. These are typically found beneath the detailed cooling capacity data chart.
Note on E24: Make sure you're NOT using the RSM load from Wrightsoft reports here. You'll want to use the RAW load data instead.
Note on I24: Many OEM's don't provide capacity data at 75 drybulb. If your's does, then choose YES here.
Note on J24: Enter the adjustment # from footnotes here, if 75/63 data is not available.
Note on E28: Input the CFM value you'll be using to describe the capacity of the equipment. For 2-stage equipment, this would be the HIGH stage.
Note on F28: This temperature should be WARMER than 63 degrees.
Note on G28: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on H28: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on F32: This temperature should be COOLER than 63 degrees.
Note on G32: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on H32: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on G39: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on H39: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on G43: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on H43: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on E60: Enter capacity from OEM data. Often called "high temp" capacity.
Note on F60: Enter capacity from OEM data. Often called "low temp" capacity.

## System9 (hidden)
Equipment Selection Analysis via Manual-S Protocols
| Completed by | #REF! |  |  |  |  | Form developed by:
#REF!
| Project Information |  |  |  |  | Design Information
| Name | #REF! |  |  |  | Outdoor Design Temperature - Summer |  |  | #REF!
| Address | #REF! |  |  |  | Indoor Design Temperature - Summer |  |  | #REF!
| City | #REF! |  |  |  | Indoor Design %RH - Summer |  |  | #REF!
| State | #REF! | Zip Code | #REF! |  | Outdoor Design Temperature - Winter |  |  | #REF!
| Permit # | #REF! |  |  |  | Project Location Elevation |  |  | #REF!
| System Name | #REF! |  |  | System Type | #REF!
| Proposed Equipment | Manufacturer |  | Furnace # |  |  |  | AFUE
|  | Manufacturer |  | AHU/Coil # |  |  |  | SEER
|  | Manufacturer |  | Condenser # |  |  |  | HSPF
|  | Manufacturer |  | Package # |  |  |  | Equip. Match-Up Adjust Factor
[8 empty] | Total | Sensible
[8 empty] | 1 | 1
| Manual J Load | Heat | Total | Sensible | Latent | SHR | Chart Indoor Dry Bulb | Is Data Available for 75DB/63WB? | Capacity Adj 1000cfm/deg
|  | Loss | BTUH | BTUH | BTUH
|  | #REF! | #REF! | #REF! | #REF! | #REF! | 80 | No
Capacity <= Design Temp | Out DB per Chart | #REF! |  | CFM | Return Air | Total | Sensible | Latent | SHR
| In DB per Chart | 80 |  |  | (F wb) | BTUH | BTUH | BTUH
| Capacity from MFG table | [6 empty] | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| Capacity from MFG table |  |  |  | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Modified for Design DB | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0!
| Capacity from MFG table | [6 empty] | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| N/A |  |  |  | 63 |  |  | 0 | #DIV/0!
| Output from this chart |  |  | 0 | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Capacity >= Design Temp | Out DB per Chart | #REF! |  | CFM | Return Air | Total | Sensible | Latent | SHR
| In DB per Chart | 80 |  |  | (F wb) | BTUH | BTUH | BTUH
| Capacity from MFG table |  |  | 0 | 0 |  |  | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| Capacity from MFG table |  |  |  | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Modified for Design DB | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0!
| Capacity from MFG table |  |  |  | 0 |  |  | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| N/A |  |  |  | 63 |  |  | 0 | #DIV/0!
| Output from this chart |  |  | 0 | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Capaicty @ Design | Out DB | #REF! |  | CFM | Return Air | Total | Sensible | Latent | SHR
| In DB | #REF! |  |  | (F wb) | BTUH | BTUH | BTUH
| Interpolated Equipment Capacity |  |  | 0 | 63 | #REF! | #REF! | #REF! | #REF!
| Excess Latent Capacity Calculation | [5 empty] | #REF! | #REF!
| Capacity @ Design Conditions | [5 empty] | #REF! | #REF! | #REF!
| Equipment Capacity as a % of Design |  |  |  |  | #REF! | #REF! | #REF!
| COOLING CAPACITY AT DESIGN CONDITIONS |  |  | CFM | Return Air WB | Total Capacity | Sensible | Latent | SHR | Alt Total | Alt Sensible
|  |  |  | 0 | 63 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Heat Pump Data (if applicable) |  |  | Capacity | Capacity | Balance | Supplimental Heat Required | Alt. Adj. Cap. @ 47 °F db | Alt. Adj. Cap. @ 17 °F db | Alt. Factor
|  |  |  | @ 47 °F db | @ 17 °F db | Point
[7 empty] | 0 | #REF! | #REF! | #REF!
| Furnace Data (if applicable) |  |  | Input | Output | AFUE | % of Load | Next Size Down? (-20kbtu input) |  | Alt. Factor
|  |  |  | Capacity | Capacity
[5 empty] | #REF! | 0 |  | N/A |  | #REF!
For instructional video, visit: HomeEnergyPartners.com/Manual-S
Note on J7: To change this field, go to the Set-Up Data Tab.
Note on J10: To change this field, go to the Set-Up Data Tab.
Note on G13: To change this field, go to the Set-Up Data Tab.
Note on I20: These are provided to adjust the capacity for a variety of equipment match-ups. These are typically found beneath the detailed cooling capacity data chart.
Note on J20: These are provided to adjust the capacity for a variety of equipment match-ups. These are typically found beneath the detailed cooling capacity data chart.
Note on E24: Make sure you're NOT using the RSM load from Wrightsoft reports here. You'll want to use the RAW load data instead.
Note on I24: Many OEM's don't provide capacity data at 75 drybulb. If your's does, then choose YES here.
Note on J24: Enter the adjustment # from footnotes here, if 75/63 data is not available.
Note on E28: Input the CFM value you'll be using to describe the capacity of the equipment. For 2-stage equipment, this would be the HIGH stage.
Note on F28: This temperature should be WARMER than 63 degrees.
Note on G28: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on H28: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on F32: This temperature should be COOLER than 63 degrees.
Note on G32: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on H32: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on G39: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on H39: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on G43: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on H43: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on E60: Enter capacity from OEM data. Often called "high temp" capacity.
Note on F60: Enter capacity from OEM data. Often called "low temp" capacity.

## System10 (hidden)
Equipment Selection Analysis via Manual-S Protocols
| Completed by | #REF! |  |  |  |  | Form developed by:
#REF!
| Project Information |  |  |  |  | Design Information
| Name | #REF! |  |  |  | Outdoor Design Temperature - Summer |  |  | #REF!
| Address | #REF! |  |  |  | Indoor Design Temperature - Summer |  |  | #REF!
| City | #REF! |  |  |  | Indoor Design %RH - Summer |  |  | #REF!
| State | #REF! | Zip Code | #REF! |  | Outdoor Design Temperature - Winter |  |  | #REF!
| Permit # | #REF! |  |  |  | Project Location Elevation |  |  | #REF!
| System Name | #REF! |  |  | System Type | #REF!
| Proposed Equipment | Manufacturer |  | Furnace # |  |  |  | AFUE
|  | Manufacturer |  | AHU/Coil # |  |  |  | SEER
|  | Manufacturer |  | Condenser # |  |  |  | HSPF
|  | Manufacturer |  | Package # |  |  |  | Equip. Match-Up Adjust Factor
[8 empty] | Total | Sensible
[8 empty] | 1 | 1
| Manual J Load | Heat | Total | Sensible | Latent | SHR | Chart Indoor Dry Bulb | Is Data Available for 75DB/63WB? | Capacity Adj 1000cfm/deg
|  | Loss | BTUH | BTUH | BTUH
|  | #REF! | #REF! | #REF! | #REF! | #REF! | 80 | No
Capacity <= Design Temp | Out DB per Chart | #REF! |  | CFM | Return Air | Total | Sensible | Latent | SHR
| In DB per Chart | 80 |  |  | (F wb) | BTUH | BTUH | BTUH
| Capacity from MFG table | [6 empty] | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| Capacity from MFG table |  |  |  | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Modified for Design DB | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0!
| Capacity from MFG table | [6 empty] | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| N/A |  |  |  | 63 |  |  | 0 | #DIV/0!
| Output from this chart |  |  | 0 | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Capacity >= Design Temp | Out DB per Chart | #REF! |  | CFM | Return Air | Total | Sensible | Latent | SHR
| In DB per Chart | 80 |  |  | (F wb) | BTUH | BTUH | BTUH
| Capacity from MFG table |  |  | 0 | 0 |  |  | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| Capacity from MFG table |  |  |  | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| Modified for Design DB | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0!
| Capacity from MFG table |  |  |  | 0 |  |  | 0 | #DIV/0!
| Modified for Design DB | [5 empty] | #REF! | #REF! | #REF!
| N/A |  |  |  | 63 |  |  | 0 | #DIV/0!
| Output from this chart |  |  | 0 | 63 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Capaicty @ Design | Out DB | #REF! |  | CFM | Return Air | Total | Sensible | Latent | SHR
| In DB | #REF! |  |  | (F wb) | BTUH | BTUH | BTUH
| Interpolated Equipment Capacity |  |  | 0 | 63 | #REF! | #REF! | #REF! | #REF!
| Excess Latent Capacity Calculation | [5 empty] | #REF! | #REF!
| Capacity @ Design Conditions | [5 empty] | #REF! | #REF! | #REF!
| Equipment Capacity as a % of Design |  |  |  |  | #REF! | #REF! | #REF!
| COOLING CAPACITY AT DESIGN CONDITIONS |  |  | CFM | Return Air WB | Total Capacity | Sensible | Latent | SHR | Alt Total | Alt Sensible
|  |  |  | 0 | 63 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Heat Pump Data (if applicable) |  |  | Capacity | Capacity | Balance | Supplimental Heat Required | Alt. Adj. Cap. @ 47 °F db | Alt. Adj. Cap. @ 17 °F db | Alt. Factor
|  |  |  | @ 47 °F db | @ 17 °F db | Point
[7 empty] | 0 | #REF! | #REF! | #REF!
| Furnace Data (if applicable) |  |  | Input | Output | AFUE | % of Load | Next Size Down? (-20kbtu input) |  | Alt. Factor
|  |  |  | Capacity | Capacity
[5 empty] | #REF! | 0 |  | N/A |  | #REF!
For instructional video, visit: HomeEnergyPartners.com/Manual-S
Note on J7: To change this field, go to the Set-Up Data Tab.
Note on J10: To change this field, go to the Set-Up Data Tab.
Note on G13: To change this field, go to the Set-Up Data Tab.
Note on I20: These are provided to adjust the capacity for a variety of equipment match-ups. These are typically found beneath the detailed cooling capacity data chart.
Note on J20: These are provided to adjust the capacity for a variety of equipment match-ups. These are typically found beneath the detailed cooling capacity data chart.
Note on E24: Make sure you're NOT using the RSM load from Wrightsoft reports here. You'll want to use the RAW load data instead.
Note on I24: Many OEM's don't provide capacity data at 75 drybulb. If your's does, then choose YES here.
Note on J24: Enter the adjustment # from footnotes here, if 75/63 data is not available.
Note on E28: Input the CFM value you'll be using to describe the capacity of the equipment. For 2-stage equipment, this would be the HIGH stage.
Note on F28: This temperature should be WARMER than 63 degrees.
Note on G28: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on H28: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on F32: This temperature should be COOLER than 63 degrees.
Note on G32: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on H32: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-24. Also, make sure it corresponds with the CFM listed in cell E-26.
Note on G39: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on H39: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on G43: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on H43: Be sure to record the capacity of the equipment at the outdoor condition listed in cell C-35. Also, make sure it corresponds with the CFM listed in cell E-37.
Note on E60: Enter capacity from OEM data. Often called "high temp" capacity.
Note on F60: Enter capacity from OEM data. Often called "low temp" capacity.